## Introduction
Pump Efficiency Calculation Tool
- Introduction
This tool calculates the energy efficiency and energy performance of water (& waste-water) pumping facilities.
Main Inputs: - Electrical energy consumption (measured or nameplate) - Run hours - Static head (from drawings) - Discharges pressure (from pressure gauge) - Flow rate (from flow meter or estimate) - Average unit price (electricity)
Main Outputs: - Motor, Pumping (Hydraulic) & System energy efficiencies - Motor, Pumping & Piping Losses - Total Energy Consumption & Energy Cost - CO2 Emissions - Energy Performance Indicators - Comparison of Actual Performance v/s Best Practice Performance Certificate
See Help worksheet for additional explanation and instructions
This tool is based on a tool originally developed by Tipperary Energy Agency, Midlands Energy Agency & Kerry County Council

## Help
Pump Efficiency Calculation Tool
- Help
This tool calculates the energy efficiency and energy performance of water (& waste-water) pumping facilities. The following Help section explains some of the Inputs, Calculations and Outputs in this tool. The Help is broken down by worksheet and can be cross referenced by row number.
Inputs Worksheet
| Row 6 | Pump / Pump Station | Name of the pump unit or pump station being analysed with this tool. Be specific: it should be clear exactly which pump system is being investigated.
| Row 10 | MPRN | A Meter Point Reference Number (MPRN) is a unique 11 digit number assigned to every single electricity connection and meter in the country. The MPRN is very important because it allows ESB Networks to track exactly where each connection on the electricity network is located (no matter who the electricity supplier is). Your MPRN number is prominently displayed on the electricity bills you receive from your Supplier. If you cannot find your MPRN number, contact your electricity supplier who will be able to check it for you.
| Rows 14-45 | Motor Power | The power consumption of the pump motor is entered in this section. You can do this in one of three alternative ways depending on what data and measurement equipment you have to hand. You can: - Enter the rated motor power directly from the nameplate (Row 17) OR - Measure the actual motor power consumption (Rows 23) OR - Measure the actual current and voltage at the motor and estimate the power factor (Row 29-35) Regardless of which of the above approaches you use, you also need to enter the motor efficiency (Row 41)
| Row 17 | Rated Motor Power | The motor's rated power is typically taken from the motor nameplate or motor documentation. If not available use one of the alternative ways to enter motor power (see below)
| Row 23 | Actual Motor Power Consumption | The actual power drawn by the motor can be measured using a wattmeter connected to the motor circuit.
| Row 29 | Motor Voltage | The Voltage of the Motor can be measured by connecting a Voltmeter across the motor.
| Row 31 | Motor Current | The Motor Current can be measured using an Ammeter.
| Row 33 | kVA | The apparent power (measured in kVA) is calculated by the spreadsheet tool using the following formula: Apparent Power (kVA) = √3 x Voltage (V) x Current (A)
| Row 35 | Power Factor (cos ѱ) | The Power Factor is typically given on the motor nameplate. If it is not available, some typical Power Factor values are given on the Inputs sheet.
| Row 41 | Motor Efficiency η Motor | The motor efficiency is typically given on the motor nameplate. If this is unavailable search the Eurodeem Motor Analysis software for the motor size and model and the database will provide an efficiency value - there is a link to this databse on the Inputs sheet. If the motor is not listed on the Eurodeem database, search the database for motors of equivalent size and use an efficeiency equal to the lowest efficiency on the database for that particular motor size, less 2%.
| Row 43 | Electrical Power Consumed | The Electric Power Consumed is equal to the power consumed while the Motor is operating. Depending on how the user enters their Motor Power Data (see row 14-45), the Electrical Power consumed is equal to either the i) Actual Motor Power (kW); ii) Motor kVA x Power Factor; iii) Rated Motor Power (kW) / Motor Efficiency (%).
| Row 45 | Motor Shaft Power | This is the mechanical power available at the output shaft of the motor; it is equal to the electrical power consumed less the motor losses (such as motor winding losses, motor inertia etc.). It is calculated automatically using the formula: Motor Shaft Power (kW) = Electrical Power Consumed (kW) x Motor Efficiency ηMotor (%)
| Row 51 | Static Suction Head | The Static Suction Head is the vertical distance between the centreline of the pump inlet and the waterline of the source. It can either be positive or negative depending on the location of the source. If the source is above the pump the Static Suction Head is negative, if the source is below the pump the value is positive.
| Row 53 | Static Discharge Head | The Static Discharge Head is the vertical distance between the centreline of the pump discharge outlet and the waterline of the reservoir or final destination that the system is pumping to. If the reservoir is above the pump the value is positive; in the unlikely event that the reservoir is below the pump, the value is negative.
| Row 55 | Pump Discharge Pressure | The Pump Discharge Pressure is the pressure measured at the discharge flange of the pump using a Pressure Gauge. The value can be entered in meters of head, bar or psi.
| Row 57 | Pump Discharge Flow Rate | The Pump Discharge Flow Rate is the flow rate measured at the pump discharge flange using a Flow Meter. It can be entered in meters cubed per hour or imperial gallons per hour (where 1 imperial gallon = 4.55 litres)
| Row 59-63 | Pump Inlet, Outlet Diameter and Velocity Head | If the Pump Inlet Diameter is not equal to the Pump Outlet Diameter the difference in velocity head across the pump has to be accounted for (this figure will generally be very small). If the Inlet and Outlet diameters are equal the Velocity Head difference will be zero .
| Row 65 | Total Head | The Total Head is the overall head supplied by the pump (both Suction Side and Discharge Side). It is calculated using the following equation: Total Head (m) = Static Suction Head (m) + Pump Discharge Head (m) + Change in Velocity Head (m) where the Change in Velocity Head is: Change in Velocity Head (m) = (Inlet Velocity - Outlet Velocity)2 (m/s)2 / 2 x g (m/s2) The Velocity is calculated using the equation: Velocity (m/s) = Flowrate (m3/h) / (Area (m2) x 3,600)
| Row 67 | Pump Hydraulic Power Output | The Pump Hydraulic Power Output is the power imparted to the fluid by the pump in kW. It is calculated using the following formula: Pump Hydraulic Power Output (kW) = (Fluid Density (kg/m3) x Acceleration due to Gravity, g (m/s2) x Total Head (m) x Flow Rate (m3/h)) / 367,000
| Row 69 | Pump Hydraulic Efficiency η Pump | This is the efficiency of the pump in turning input shaft power (from the motor) into useful power output to the fluid (Hydraulic Power), it is calculated using the following formula: Pump Hydraulic Efficiency (%) = Pump Hydraulic Power Output (kW) x 100 / Pump Input Shaft Power (kW). The Pump Input Shaft Power is the same as the Motor Shaft Power
| Row 71 | System Friction Losses (Discharge Side) | These are the due to internal friction in the system piping on the Discharge Side of the pump. They are calculated using the following formula: System Friction Losses (m) = Pump Discharge Pressure (m) - Static Discharge Head (m)
| Row 112 | Electricity Average Unit Price (AUP) | The AUP can be calculated from eletricity bills - it is the total amount charged (in €) in a period (including standing charges) divided by the total number of units used in that period .
| Row 114 | CO2 Emission Factor (Electricity) | Different electricity suppliers have different Emission Factors, which reflect the different generation mixes from which the suppliers source their electricity. The Emission Factor is usually given on the electricity bill or can be provided on request by the electricity supplier. The average national emission factor is shown on the spreadsheet and may be used if the supplier specific value is unknown.
| Row 116 | Fluid Density | Density of the fluid being pumped in kg/m3.
| Row 118 | Length of pipe | The length of piping in the pumping system in kilometres. This can be determined from system drawings or estimated.
| Row 120 | Best Practice: Motor Efficiency | This value is equivalent to the highest efficiency motor available on the market, equal in size to the motor in use in the system being analysed. To obtain a value search the Eurodeem Database for an EFF1 (High Efficiency) motor of equivalent size to the one in use in the pumping system being analysed, and use its motor efficiency value as the Best Practise Value.
| Row 127 | Best Practice: Pump Hydraulic Efficiency | This is equivalent to the highest value currently attainable in industry. Typical values are available from the Pumping System Assessment Tool (PSAT). Enter the system data into PSAT and PSAT will provide an "Optimal Efficiency" value for the Pump Efficiency, input this value as Best Practice.
| Row 129 | Best Practice: Design Friction Losses | The Friction Losses that the system was desgned for (in meters of head per kilometre of pipeline), if known. If unknown, some typical values are provided or use the Pressure Drop Calculator (link provided) to calculate the system pressure drop.
Summary Worksheet
| Row 14 | "Piping" Efficiency | The "Piping" Efficiency is the efficiency of the system pipework and is influenced by variables such as pipe internal roughness and leakages. For the purposes of this tool the "Piping" Efficiency is assumed to be equal to the efficiency of the discharge side piping and does not take into account the suction side pipework. The "Piping" Efficiency therefore is calculated using the following formula: "Piping" Efficiency (%) = (Pump Discharge Pressure - Static Discharge Head) / Pump Discharge Head)
| Row 16 | Overall System Efficiency | The Overall System Efficiency (%) is calculated by using the following formula: Overall System Efficiency (%) = Motor Efficiency (%) x Pump Hydraulic Efficiency (%) x "Piping" Efficiency (%)
| Row 21 | Electricity Consumed p.a. | Electricity Consumed p.a. (kWh) = Electricial Power Consumed (kW) x Operating Hours p.a (h)
| Row 23 | Electricity Cost p.a. | Electricity Cost p.a. (€) = Electricity Consumed p.a (kWh) x Electricity Average Unit Price (€/kWh)
| Row 25 | Volume of Fluid Displaced p.a. | Volume of Fluid Displaced p.a. (m3) = Pump Discharge Flowrate (m3/h) x Operating Hours p.a. (h)
| Row 27 | kgCO2 Emitted p.a | kgCO2 Emitted p.a. = Electricity Consumed p.a. (kWh) x Emission Factor (kgCO2/kWh)
| Row 35 | Motor Loss | Motor Loss (%) = 1 - Motor Efficiency (%)
| Row 37 | Pumping Loss | Pumping Loss (%) = 1 - Pump Efficency (%)
| Row 39 | Friction Loss | Friction Loss (%) = 1 - "Piping" Efficiency (%)
| Row 41 | Total Losses | Total Losses (%) = Motor Loss (%) + Pumping Loss (%) + Friction Loss (%)
| Row 43 | Useful Work Done | Useful Work Done (%) = Overall Efficiency (%)
Performance Certificate
EPIs are useful for comparison purposes to allow plant operators to compare their performance both internally (i.e. internal benchmarking over a period of time) and externally (to that of other plants). Caution should be exercised when comparing EPIs as they are plant specific and are influenced by variables such as plant size, total static head, motor efficiencies etc. Below is a list of some of the more common Wastewater and Pumping EPIs and a brief description of each one.
|  | kWh/m3 | This is the most commonly used EPI in water pumping applications. It is particularly useful for monitoring energy performance at one facility over time. It is less useful for comparison purposes because comparisons are only valid for plants with similar design & operating parameters.
|  | kWh/1,000m3/m | This is useful for internal comparison and, importantly, for compating performance between different plants because it account for differences in static head.
|  | €/m3 | Care should be taken when comparing to values for other stations as this EPI is dependent on the AUP for electricity which is dependent on the electricity supplier and may change from plant to plant and from time to time.
|  | kgCO2/kWh | Care should be taken when comparing to values for other stations as this EPI is dependent on the emission factor, which may vary from plant to plant and from time to time.
This tool is based on a tool originally developed by Tipperary Energy Agency, Midlands Energy Agency & Kerry County Council

## Inputs
Pump Efficiency Calculation Tool
- Inputs
| Pump / Pump Station | :
| Location | :
| MPRN | :
| Date | : |  |  | ENTER DATA IN THESE CELLS ONLY
MOTOR
This section calculates the efficiency of the motor that drives the pump. You can enter the motor power from the nameplate data or from measurement (meter)
| Rated Motor Power | : |  | kW | Enter from nameplate, if rated in Horsepower, use 1 HP = 0.746 kW
or
| Actual Motor Power Consumption | : |  | kW | From measurement (meter)
or
| Voltage | : |  | V | From measurement (meter)
| Current | : |  | A | From measurement (meter)
| kVA | : | 0 | kVA
| Power factor (cos ѱ) | : |  |  | If VSD, then = 1 ¦ Non-VSD Maximum = 0.83 ¦ Non-VSD Typical Full Load = 0.78-0.81 ¦ Non-VSD Typical Half Load = 0.70
and
| Motor Efficiency η Motor | : |  |  | From manufacturer's data sheets (try www search for motor type)
If not available, use lowest efficiency from EuroDEEM database less 2%. (Click here to download EuroDEEM software for free)
| Electrical Power Consumed | : | 0 | kW
| Motor Shaft Power | : | 0 | kW | = Pump Shaft Power
PUMP
This section calculates the hydraulic efficiency of the pump and the losses in the system pipework. You need to enter the static head (from drawings or estimates),the pump discharge pressure (from pressure gauge) and the flow rate (from a flowmeter or estimate).
| Static Suction Head | : |  | m of head | From drawings: vertical distance from surface of source reservoir / borehole / vessel to centreline of pump ¦ +ve if source below pump ¦ -ve if source above pump
| Static Discharge Head | : |  | m of head | From drawings: vertical distance from centreline of pump to surface of delivery reservoir / vessel
| Pump Discharge Pressure | : |  | m of head | From measurement (pressure gauge) @ pump discharge flange
| Pump Discharge Flow Rate | : |  | m3/h | From measurement (flowmeter) @ pump discharge or estimate
| Is Inlet Diameter = Outlet Diameter? | : | Yes |  | If No, enter Pump Inlet & Outlet Diameters below
| Pump Inlet Diameter | : |  | m | Leave this field blank
| Pump Outlet Diameter | : |  | m | Leave this field blank
| Total Head | : | 0 | m of head | Static Suction Head (m hd) + Pump Discharge Head (m hd) + Velocity Head Difference (m hd)
| Pump Hydraulic Power Output | : | 0 | kW | = Flow Rate x Density x g x Total Head / 3.6 x 106
| Pump Hydraulic Efficiency η Pump | : | -
| System Friction Losses (Discharge Side) | : | 0 | m of head | = Pump Discharge Head - Static Discharge Head
0
m
m3/h
0
0
NOTE: The Pump Inlet and Pump Discharge Flanges may or may not be be at the same level. The Calculation Tool does not account for such an elevation difference, it assumes the Pump Inlet and the Pump Outlet are at the same level.
OTHER PARAMETERS
These parameters should be relatively straightforward to enter.
| Electricity Average Unit Price | : |  | €/kWh
| CO2 Emission Factor (Electricity) | : | 0.625 | kgCO2/kWh | 2007 SEI Average Generation Mix = 0.625 kgCO2/kWh
| Fluid Density | : | 1000 | kg/m3 | Water = 1,000 kg/m3 ¦ Medium strength wastewater ~ 1,030 kg/m3
| Length of Pipe (Discharge Side) | : |  | km
| Operating Hours pa | : |  | hours/year | Operating hours per annum
BEST PRACTICE VALUES
These values are only used to compare your pump's performance with Best Practice. They are not required to calculate your pump's performance / efficiency.
| Motor Efficiency | : |  |  | Full Load Efficiency from EuroDEEM (click here) for motor of your size (or use the benchmark motor)
| Pump Hydraulic Efficiency | : |  |  | Use ~85% value or download PSAT (click here) for typical achievable values
| Design Friction Losses (Discharge Side) | : |  | m hd per km of pipe | For an 18" concrete pipe losses range from 0.4 - 1.3m head per km for flow of ~250-450 m3/hour (~20%-30% less for plastic pipe). Online pressure calculator available from Pressure-Drop.com (click here & then click Pressure Drop Online Calculator).
This tool is based on a tool originally developed by Tipperary Energy Agency, Midlands Energy Agency & Kerry County Council

## Summary
Pump Efficiency Calculation Tool
- Performance Summary
EFFICIENCIES
|  |  | Actual | Best Practice
| Motor Efficiency | : | 0% | 0%
| Pump Hydraulic Efficiency | : | - | 0%
| "Piping" Efficiency | : | #DIV/0! | #DIV/0!
| Overall System Efficiency | : | #DIV/0! | #DIV/0!
ENERGY SUMMARY
| Electricity consumption p.a | : | 0 | kWh
| Electricity cost p.a | : | 0
| Volume of fluid displaced p.a | : | 0 | m3
| kgCO2 Emitted p.a | : | 0 | kgCO2
ENERGY LOSSES
|  |  | Actual % | Best Practice % | Actual kWhE per annum | Actual Cost per annum
| Motor Loss | : | 100% | 100% | 0 | 0
| Pumping Loss | : | #VALUE! | 100% | #VALUE! | #VALUE!
| Friction Loss | : | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0!
| Total Losses | : | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Useful work done | : | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
ENERGY PERFORMANCE INDICATORS (EPIs)
| #DIV/0! |  | KWh/m3 |  | #DIV/0! | kWh/1,000m3/m
| #DIV/0! |  | €/m3 |  | #DIV/0! | €/1,000m3/m
| #DIV/0! |  | kgCO2/m3 |  | #DIV/0! | kgCO2/1,000m3/m
This tool is based on a tool originally developed by Tipperary Energy Agency, Midlands Energy Agency & Kerry County Council

## Performance Certificate
Pump Efficiency Calculation Tool
- Performance Certificate
| Site Name | : | 0
| Location | : | 0
| Date of Issue | : |  |  | EPIs
| Valid Until | : | - |  | kWh/m3 | #DIV/0!
[5 empty] | kWh/1,000m3/m | #DIV/0!
| CONSUMPTION, COST & CO2 EMISSIONS |  |  |  | €/m3 | #DIV/0!
| Annual Electricity Consumption: |  | 0 | kWh | €/1,000m3/m | #DIV/0!
| Annual Electricity Cost: |  | 0 |  | kgCO2/m3 | #DIV/0!
| Annual CO2 Emissions: |  | 0 | kgCO2 | kgCO2/1,000m3/m | #DIV/0!
PERFORMANCE CLASSIFICATION
|  |  |  | Overall Efficiency | Pump Efficiency | kWh/1,000m3/m
|  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
BEST PRACTICE & LOSSES
This tool is based on a tool originally developed by Tipperary Energy Agency, Midlands Energy Agency & Kerry County Council
B >65%
D >45%
E >35%
F >25%
C >55%
G <25%
A >70%

## Version
Pump Efficiency Calculation Tool Version History
Version | Description of Modification(s) | Date | Additional Comments
1 |  | 2009-10-14 | Issued to PK (TEA) for review & comment
2 | Improved formatting Inclusion of TEA & MEA logos Relocation of Power Factor row | 2009-10-22 | Issued to WS Working Group for Review & Comment
3 | Update of Static Head calculation Help worksheet | 2010-03-03 | Issued to SEI
4 | Change to calculation of friction loss Formatting Changes | 2010-03-05 | Issued to SEI & WS WG
5 | Included reference to Kerry Co Co Rebranded SEAI | 2010-03-22 | Issued to SEAI & WS WG
This tool is based on a tool originally developed by Tipperary Energy Agency, Midlands Energy Agency & Kerry County Coucil

## Fixed Data (hidden)
| Drop down menu selections | m of head | m3/h | m hd per km of pipe | Yes | Conversion Factors |  | Efficiencies | 70% | Motor Losses | 0
|  | bar | g/h | bar per km of pipe | No | bar | m of head |  | 65% | Pumping Losses | #VALUE!
|  | psi |  |  |  | 1 | 10.197 |  | 55% | Friction Losses | #VALUE!
[9 empty] | 45% | Useful work done | #DIV/0!
| Parameter | Value |  |  |  | psi | m of head |  | 35%
| g (Acceleration due to gravity) | 9.81 | m/s |  |  | 1 | 0.70325 |  | 25%
25%
| Hydraulic power static discharge(m hd) | 0 | kW |  |  | g/h | m3/h
| Hydraulic power static discharge (bar) | 0 | kW |  |  | 1 | 0.0045461
| Hydraulic power static discharge (psi) | 0 | kW
| Hydraulic power static suction (m hd) | 0 | kW
| Hydraulic power static suction (bar) | 0 | kW
| Hydraulic power static suction (psi) | 0 | kW
| Velocity Hydraulic Power (m hd) | 0 | kW
| Velocity Hydraulic Power (bar) | 0 | kW
| Velocity Hydraulic Power (psi) | 0 | kW
| Pump Discharge hydraulic power (m hd) (m3/h) | 0 | kW
| Pump Discharge hydraulic power (bar) (m3/h) | 0 | kW
| Pump Discharge hydraulic power (psi) (m3/h) | 0 | kW
| Hydraulic power total (Static Suction + Pump Discharge Head + Delta Vel) (m hd) m3/h | 0 | kW
| Hydraulic power total (Static Suction + Pump Discharge Head + Delta Vel) (bar) m3/h | 0 | kW
| Hydraulic power total (Static Suction + Pump Discharge Head + Delta Vel) (psi) m3/h | 0 | kW
| Hydraulic power total (Static Suction + Pump Discharge Head + Delta Vel) (m hd) g/h | 0 | kW
| Hydraulic power total (Static Suction + Pump Discharge Head + Delta Vel) (bar) g/h | 0 | kW
Each calc used for each dropdown (m hd, bar, psi), in Input Sheet | Hydraulic power total (Static Suction + Pump Discharge Head + Delta Vel) (psi) g/h | 0 | kW
| Delta Velocity Head | 0 | m
| Hydraulic power friction (m hd) | 0 | kW
| Hydraulic power friction (bar) | 0 | kW
| Hydraulic power friction (psi) | 0 | kW
Used for converting the pump dischrge pressure from m hd, bar & psi inot m hd for system friction losses calculation | Pump Discharge Pressure (m hd) | 0 | m hd
| Pump Discharge Pressure (bar) | 0 | m hd
| Pump Discharge Pressure (psi) | 0 | m hd
| Pump discharge m hd | 0 | m hd
| Velocity Head Inlet | 0 | m
| Velocity Head Outlet | 0 | m
| Inlet Velocity | 0 | m/s
| Outlet Velocity | 0 | m/s